## Slide 1
Sharad Institute of Technology, College of Engineering, Yadrav.
Department of Mechanical Engineering.
APPLIED THERMODYNAMICS
STEAM CONDENSER AND COOLING TOWER (UNIT 3)

## Slide 2: CONDENSATION
If the pressure of the exhaust steam reduced below the atmospheric pressure and hence its energy, partially of fully, can not be reutilized, than this phenomenon is called Steam Condensation.

## Slide 3: STEAM CONDENSERS
The heat transfer device in which the exhaust steam of a turbine or an engine is condensed by means of cooling water at pressure below atmospheric, is called Steam Condenser.

## Slide 4: CONDENSATE
The condensed Steam is called Condensate and can be again returned to Boiler. It saves the cost of water.

## Slide 5: PRINCIPLE OF CONDENSATION
In order to attain maximum work, according to Carnot principle, the heat must be supplied at Maximum pressure and temperature and should be rejected at Minimum pressure and temperature.

## Slide 6: PRINCIPLE OF CONDENSATION
The steam from the steam turbine or steam engine could be exhausted to atmosphere in such a manner that the back pressure would below the atmospheric pressure.

## Slide 7: ADVANTAGES OF CONDENSERS
It increases the work output per kg of steam supplied to the power plant.
Reduces the specific steam consumption.
Reduces the size of power plant of given capacity.
Improves the thermal efficiency of power plant.
Saves the cost of water to be supplied to boiler.

## Slide 8: ELEMENTS OF CONDENSING PLANT
CONDENSER: In which the exhaust steam of the turbine is condensed by circulating cooling water.
CONDENSATE EXTRACTION PUMP: to remove the condensate from the condenser and feed it into the hot-well. The feed water from hot-well is further pumped to boiler.

## Slide 9: ELEMENTS OF CONDENSING PLANT
AIR EXTRACTION PUMP: to remove air from the condenser, such a pump is called dry air pump. If air and condensate both are removed, it is called as wet air pump.
CIRCULATING PUMP: used to supply feed water either from river or from the cooling tower pond to the condenser.

## Slide 10: ELEMENTS OF CONDENSING PLANT
COOLING TOWER:
The Ferro concrete made device (hyperbolic shape) in which the hot water from the condenser is cooled by rejecting heat to current of air passing in the counter direction.
Ring troughs are placed 8-10m above the ground level.

## Slide 11: TYPES OF CONDENSERS
JET CONDENSERS
The exhaust steam and cooling water come in direct contact and as a result the steam is condensed. It is also called direct contact condensers.
SURFACE CONDENSERS
The cooling water flows through a network of tubes and the exhaust steam passes over these tubes. The steam gets condensed due to heat transfer to coolant by conduction and convection.

## Slide 12: COMPARISION
S.No | Jet condensers
1. | Steam and water comes in direct contact.
2. | Condensation is due to mixing of coolant.
3. | Condensate is not fit for use as boiler feed until the treated cooling water is supplied.
4. | It is cheap. Does not affect plant efficiency.
5. | Maintenance cost is low.
6. | Vacuum created is up to 600 mm of Hg.
Surface condensers
Steam and water does not come in direct contact.
Condensation is due to heat transfer by conduction and convection.
Condensate is fit for reuse as boiler feed.
It is costly. Improves the plant efficiency.
Maintenance cost is high.
Vacuum created is up to 730 mm of Hg.

## Slide 13: JET CONDENSERS

## Slide 14: CLASSIFICATION OF JET CONDENSERS
Low level jet condensers
Counter flow type
Parallel flow type
2. High level jet injectors
3. Ejector jet condensers

## Slide 15: 1.(i) LOW LEVEL COUNTER FLOW JET INJECTOR
The cooling water to be lifted into the condenser up to a height of 5.5m.
It is having disadvantage of flooding the steam turbine if the condensate extraction pump fails.

## Slide 16: 1.(ii) LOW LEVEL PARALLEL FLOW JET INJECTOR
The mixture of condensate, coolant and air are extracted with the help of wet air pump.
Vacuum created in the condenser limits up to 600 mm of Hg.

## Slide 17: 2. HIGH LEVEL JET CONEDNSER/ BAROMETRIC JET CONDENSER
It is also called Barometric jet condenser since it is placed above the atmospheric pressure equivalent to 10.33 m of water pressure.
Condensate extraction pump is not required because tail pipe has incorporated in place of it.

## Slide 18: 3. EJECTOR JET CONDENSER
The cooling water enters the top of the condenser at least under a head of 6m of water pressure with the help of centrifugal pump.
This system is simple, reliable and cheap.
Disadvantage of mixing of condensate with the coolant.

## Slide 19: SURFACE CONDENSERS

## Slide 20: Surface condensers are of two types
SURFACE CONDENSERS
In this steam flows outside the network of tubes and water flows inside the tubes.
EVAPORATIVE CONDENSERS
In this condenser shell is omitted. The steam passes through condenser tubes, the water is sprayed while the air passes upward outside the tube.

## Slide 21: CLASSIFICATION OF SURFACE CONDENSERS
The number of water passes:
Single pass
Multipass
The direction of condensate flow and tube arrangement:
Down flow condenser
Central flow condenser

## Slide 22: DOUBLE PASS SURFACE CONDENSER
It consist of air tight cast iron cylindrical shell.
If cooling water is impure, condenser tubes are made up of red brass.

## Slide 23: DOWN FLOW SURFACE CONDENSER
This condenser employs two separate pumps for the extraction of condensate and the air.
Baffles are provided so that the air is cooled to the minimum temperature before it is extracted.
The specific volume of cooled air reduces, thereby, reduces the pump capacity to about 50%. Therefore, it also reduces the energy consumption fro running the air pump.

## Slide 24: CENTRAL FLOW SURFACE CONDENSER
Air extraction pump is located at the centre of the condenser tubes.
Condensate is extracted from the bottom of the condenser with the help of condensate extraction pump.
Provides the better contact of steam.

## Slide 25: EVAPORATIVE CONDENSER
The exhaust steam is passed through the series of gilled tubes called condenser coils.
Thin film of cooling water trickles over these tubes continuously from water nozzles.
During the condensation of steam, this thin film of water is evaporated and the remainder water is collected in the water tank.
The condensate is extracted with the help of wet air pump.
The air passing over the tubes carries the evaporated water in the form of vapour and it is removed with the help of induced draft fan installed at the top.

## Slide 26: MERITS AND DEMERITS OF JET CONDENSERS
MERITS
Less quantity of cooling water is required to condense the steam.
Simple in construction and low in cost.
Does not require cooling water pump.
Less space is required.
Low maintenance cost.
DEMERITS
The condensate is a waste.
Less suitable for high capacity plants.
Large length of pipes required, hence piping cost is high.
Loss of vacuum due to leakage of air from long pipings.

## Slide 27: MERITS AND DEMERITS OF SURFACE CONDENSERS
MERITS
No mixing of cooling water and steam, hence the condensate directly pumped into the boiler.
Any kind of feed water can be used.
Develops high vacuum, therefore suitable fro large power plants.
Require less power to run the air extraction and water extraction pump.
System is more efficient.
DEMERITS
Require large quantity of cooling water.
System is complicated, costly and requires high maintenance cost.
Require large floor space since it is bulky.

## Slide 28: AIR PUMPS

## Slide 29: TYPES OF AIR PUMPS
WET AIR PUMP
DRY AIR PUMP

## Slide 30: AIR PUMPS
WET AIR PUMP
Used to remove both condensate and the air from the condenser. These may be of type:
Reciprocating
Rotary
DRY AIR PUMP
Used only to remove moist air. These may be of type:
Reciprocating
Rotary

## Slide 31: RECIPROCATING AIR PUMP (Edward’s Air Pump)
This pump is suitable only for small power plants.

## Slide 32: STEAM JET AIR EJECTOR
It consists of convergent- divergent nozzle and a diffuser.
Steam from boiler enters from ‘a’ nozzle where its K.E increases and pressure decreases.
Pipe ‘c’ is connected to condenser form where the air mixes with low pressure steam at ‘b’.
The mixture of steam and air moves to diffuser ‘d’ where its velocity decreases and pressure increases at the time of leaving.

## Slide 33: STEAM JET AIR EJECTOR
The system shows only one ejector, if more ejectors are introduced, a very low pressure can be obtained in the condenser.
Usually up to four numbers of ejectors are used which can reduce the pressure in the condenser up to 0.08 bar.
It is simple in construction, cheap, highly efficient and don’t have any moving parts.

## Slide 34: DALTONS LAW OF PARTIAL PRESSURE
“The total pressure exerted by mixture of gases or a mixture of gas and vapors (which have no chemical action on each other) is equal to the sum of the partial pressures of the constituents of the mixture, if it occupies the volume of mixture at temperature of mixture”.

## Slide 35: DALTONS LAW OF PARTIAL PRESSURE
The total pressure in the condenser is the sum of the partial pressure of steam and air.
Pressure of mixture= partial pressure of steam + partial pressure of air
So according to Daltons law total pressure in the condenser is,
Pc = Ps + Pa
Where , Pc= total pressure in condenser
Ps= partial pressure of steam
Pa= partial pressure of air.

## Slide 36: DALTONS LAW OF PARTIAL PRESSURE
Steam + air
steam
Air
Pc
Ps
Pa

## Slide 37: Steam condenser
A steam condenser is a closed vessel in to which the steam is exhausted, and condensed after doing work in an engine cylinder or turbine.
A steam condenser has the following two object:
1) the primary object is to maintain a low pressure (below atmospheric pressure) so as to obtain maximum possible energy from steam and thus to secure high efficiency.
2) the secondary object is to supply pure feed water to the hot well, from where it is pumped back to boiler.

## Slide 38: Classification of steam condenser
The steam condensers may be broadly classified in to the following two types, depending upon the way in which the steam is condensed.
1) jet condensers or mixing type condensers
Parallel flow jet condenser
Counter flow jet condenser
Barometric or high level jet condenser
Ejector condenser.
2) surface condensers or non mixing type condensers.
A) Down flow surface condenser
B) central flow surface condenser
C) Regenerative surface condenser
D)evaporative condenser

## Slide 39: Surface condenser
A surface condenser has a great advantages over the jet condenser, as the condensate does not mix up with cooling water.
As a result of this whole condensate can be reused in the boiler.
This type of condenser is essential in ships which can carry only a limited quantity of fresh water for the boilers.
Fig . Shows a longitudinal section of a two pass surface condenser.

## Slide 40: Surface condenser

## Slide 41: Surface condenser
It consist of a horizontal cast iron cylindrical vessel packed with tubes, through which the cooling water flows.
The end of the condensers are cut off by vertical perforated types of plates in to which water tubes are fixed.
This is done in such a manner that the leakage of water into the centre condensing space is prevented.
The water tubes pass horizontally through the main condensing space for the steam.

## Slide 42: Surface condenser
The steam enters at the top and is forced to flow down words over the tubes due to the suction of the extraction pump at the bottom.
The cooling water flows in one direction through the lower half of the tubes and returns in opposite direction through the upper half.

## Slide 43: Source of air leakage
The following are main sources through which the air may enter in to the condenser:
The dissolved air in the feed water enters in to the boiler, which in turn enters in to the condenser with exhaust steam.
The air leaks in to the condenser, through various joint, due to high vacuum pressure in the condenser.
In case of jet condensers , dissolved air with the injection water enters in to the condenser.

## Slide 44: Effect of air leakage
It reduces vacuum pressure in the condenser.
Since air is poor heat conductor, particularly at low densities, it reduces the rate of heat transmission.
It requires a larger air pump. Moreover, an increased power is required power is required to drive the pump.

## Slide 45: Condenser efficiency
The condenser efficiency may be defined as the ratio of temperature rise of cooling water to the vacuum temperature minus inlet cooling water temperature.
ᶯc = temperature rise of cooling water/(vacuum temperature- inlet cooling water temperature)
ᶯc = (to – ti ) / (tv-ti)
Where, to= outlet temperature of cooling water.
ti= inlet temperature of cooling water.
tv= vacuum temperature

## Slide 46: Vacuum efficiency
The minimum absolute pressure (also called as ideal pressure) at the steam inlet of a condenser is the pressure corresponding to the temperature of the condensed steam.
The corresponding vacuum (called ideal vacuum) is the maximum vacuum that can be obtained in a condensing plant, with no air present at that temperature.
The pressure in the actual condenser is greater than the ideal pressure by an amount equal to the pressure of air present in the condenser.
The ratio of the actual vacuum to the ideal vacuum is known as vacuum efficiency.

## Slide 47: Vacuum efficiency
ᶯv= actual vacuum /ideal vacuum
Actual vacuum= barometric pressure- actual pressure
Ideal vacuum = barometric pressure- ideal pressure

## Slide 48: Cooling tower
The main application are in power plants and refrigeration plants.
Its function is to cool the hot water from the condenser by exposing it to the atmospheric air, so that the cold water may be used again for circulation.
The cooling towers are used in steam power plants where there is a limited supply of cooling water.
It is placed at a certain height (at about 9 meters from the ground level).

## Slide 49: Cooling tower
The hot water falls down in radial sprays from a height and the atmospheric air enters from the base of tower.
The partial evaporation of water takes place which reduces the temperature of circulating water.
This cooled water is collected in the pond at the base of the tower and pumped in to the condenser.

## Slide 50: Types of cooling tower
1) Natural draught cooling tower
The circulation of air is produced by the pressure difference of air inside and outside the cooling tower.
2) Forced draught cooling tower
The circulation of air is produced by means of fans placed at the base of tower.
3) Induced draught cooling tower
The circulation of air is provided by means of fan placed at top of tower.

## Slide 51: Natural draught cooling tower

## Slide 52: Forced water cooling tower

## Slide 53: Induced draught cooling tower
Notes: <number>