## Slide 1
Sharad Institute of Technology, College of Engineering, Yadrav.
Department of Mechanical Engineering.
APPLIED THERMODYNAMICS
STEAM TURBINE (UNIT 5,6)

## Slide 2
Sharad Institute of Technology, College of Engineering, Yadrav.
Department of Mechanical Engineering.
APPLIED THERMODYNAMICS
STEAM TURBINE (UNIT 5,6)
Mr.Avesahemad S.N. Husainy

## Slide 3: Input Parameters for Selecting the Design
For the design and construction of the steam path of a turbine, the following parameters are usually specified.
Nominal Electric Power of turbo generator.
Initial parameters of steam, p3 &T3.
Parameters of reheated steam, prh & Trh.
Pressure of condenser, p4.
Temperature of feed water at the exit from final FWH, Tfwh.
Rotational speed of the turbine Rotor, N.

## Slide 4: Design of Steam Path
Assume an overall isentropic efficiency of the turbine and estimate approximate mass flow rate of steam (iso = %).
The design of turbine stages and the dimensions of turbine elements in the steam path depend substantially on the volume discharge of steam.
In a typical turbine the specific volume increases 2500 times along the steam path.
In view of the specifics of the steam path design, all the stages of a steam turbine are divided into four groups.
Governing stage
Low volume stages (HP Turbine Drum).
Intermediated volume stages (IP Turbine Drum).
Very high volume stages (LP Turbine Drums).

## Slide 5: Typical Modern Power Plant Turbine

## Slide 6: HP Turbine Rotor

## Slide 7: LP Turbine Rotor

## Slide 8
LP Turbine Rotor

## Slide 9: Diagram of Large Power Plant Turbine

## Slide 10: Block Diagram of A Large Steam Turbine
Condenser
Reheat Steam
HP
Main Steam
Steam for
Reheating
IP
IP
LP
LP
CFWH 6
CFWH 5
OFWH 4
CFWH 2
CFWH 1
CFWH 3

## Slide 12: Governing Stage
A governing stage is the first stage in a turbine with nozzle steam distribution.
The principal design feature of a governing stage is that its degree of partiality changes with variations of flow rate through the turbine.
The nozzles of a governing stages are combined into groups, each of them being supplied with steam from a separate governing valve.
A governing stage is separated by a spacious chamber from the subsequent non-controlled stages.
Governing stages may be of a single-row or two-row type.
Single row impulse governing stage is employed for an enthalpy drop of 80-120 kJ/kg.
Two row governing stages are used when enthalpy drop is high, 100 – 250 kJ/kg.

## Slide 13: Selection of Enthalpy Drop & Type of Governing stage
The enthalpy drop & type of governing stages are selected by considering the probable effect of the governing stage on the design and efficiency of the turbine.
Higher the number of governing stages, lower will be the number of other stages.
A high enthalpy drop in governing stage ensures a lower temperature of steam in its chamber and permits application of less expensive materials.
In high capacity steam turbines, a single-row governing stages are preferred, since the advantages of elevated enthalpy drop are justified economically.
The efficiency of governing stages,

## Slide 14: Steam Path in Non-Controlled Stages
Estimate approximate mass flow rate of steam by assuming an overall turbine internal efficiency of 0.85.
Calculate flow through the condenser, using optimum of number of FWHs. (Using Cycle Calculations).
Calculate Modified Efficiency of Low volume and intermediate volume stages.
For a group of stages between two successive FWHs.
Average mass flow rate and average density are calculated as

## Slide 15
The efficiency of groups of very high volume stages:
While designing the steam path, it is essential to consider the pressure losses in the following:
Pressure loss in reheater: 0.1 prh.
Pressure loss in connecting pipes between turbine cylinders:0.2ppipe.

## Slide 16: Internal Reheating due to Irreversibilities
3
4s
4IIs
4IIIs
4Is
4Vs
4IVs
4Ia
4IIa
4IIIa
4IVa
4Va
4VIs
4VIa
T
s
Governing group
Group 1
Group 2
Group 3
Group 4
Group 5

## Slide 17: Determination of The Height of Moving Blades
The entrance height of moving blade is made slightly larger than the height of the nozzle.
For short blades lm is made larger by about 2 to 4 mm.
For tall blades this difference is greater than 4mm.
The exit cross section of the moving blades in a direction perpendicular to the direction of relative exit velocity vector is
Exit cross section in the plane of rotation of disc
ln
lm

d

## Slide 18
Afm is also expressed as
tm
am
e
e

## Slide 19
How to decide about the width of
The Blades?
The widths of the nozzle & moving
blade is immaterial for an Isentropic
flow!
Losses decide the widths……
wn
wm

## Slide 20: Irreversibilities in Turbine
T
s
3
4s
4a
Ideal work ws = h3 – h4s
Actual work wa = h3 – h4a
Internal Efficiency of a turbine

## Slide 21: Losses in Turbine
Losses in Regulating valves : The magnitude of loss of pressure due to throttling with the regulating valves fully open is:
pv = 3 to 5% of pmax.
Loss in nozzle blades.
pressure loss in moving blades.
Loss due to exit velocity.
Loss due to friction of the disc and blade banding
Loss associated with partial admission.
Loss due to steam leakages through clearances.
Loss due to flow of wet steam.
Loss due to exhaust piping.
Loss due to steam leakage in seals.

## Slide 22: Losses in Nozzles
Losses of kinetic energy of steam while flowing through nozzles or guide blade passages are caused because of
  Energy losses of steam before entering the nozzles,
  Frictional resistance of the nozzles walls,
  Viscous friction between steam molecules,
  Deflection of the flow,
  Growth of boundary layer,
  Turbulence in the Wake and
  Losses at the roof and floor of the nozzles.
These losses are accounted by the velocity coefficient, .

## Slide 23
Blade Height

## Slide 24: Losses in Moving Blades
Losses in moving blades are caused due to various factors.
The total losses in moving blades are accounted for by the velocity coefficient, ψ.
These total losses are comprised of the following:
Losses due to trailing edge wake.
Impingement losses.
Losses due to leakage of steam through the annular space between stator and the shrouding.
Friction losses.
Losses due to the turning of the steam jet in the blades
..Losses due to shrouding.

## Slide 26
Blade Height

## Slide 27: Leaving Velocity (Carry-over) Losses
Steam leaves the exit of moving blades with an absolute velocity of Vae.
In multi stage turbines the velocity energy of the exit steam may be used either in fully or partially in succeeding stages.
The energy loss due to leaving velocity:

## Slide 28: Losses due to Disc Friction and Windage
Frictional forces appear between the rotating turbine disc and the steam enveloping it.
The rotating disc drags the particles near its surface and imparts to them an accelerating force in the direction of rotation.
A definite amount of mechanical work is spent in overcoming the effect of friction and imparting this acceleration.
In the case of partial admission there is good deal of turbulence over the arc where steam is not admitted.
This turbulence causes windage losses which basically consist of the following:
  Friction & Impingement of steam on the blades.
  Intermittent admission of steam into the moving blades.

## Slide 29
The magnitude of these losses is calculated using Stodola’s Emperical Formula:
Nwind: Power los in overcoming friction and windage.
λ : fluid Coefficient: 1 for air or highly superheated steam, 1.1 – 1.2 for ordinary superheated & 1.3 for saturated steam.
d : Mean diameter of the disc.
z: Number of velocity stages.
ε: Degree of partial admission.
l1: Heght of blades, in cm.
U : Velocity of blade at mean diameter, m/s.
ρ: density of steam, kg/m3.

## Slide 30: Clearances Losses
The value of gap δr is chosen in such a way so that during operation of turbine the blades of turbine both moving and fixed donot scrap against the stator and rotor respectively.
Pressure difference across fixed and/or moving blades leads to leakage of steam through the gap.
This leakage leads to loss of mechanical power.
Empirical Formula:

## Slide 31: Losses due to Wetness of Steam
The absolute velocity of water droplets is generally less than that of steam.
The direction of relative velocity of water droplets is not tangential to the blade.
The water droplets are deflected onto the back of the moving blades as a result of which the moving blades experience an impact force.

## Slide 32: Exhaust Piping Losses
Loss of pressure in exhaust pipings of condensing turbines may be determined from:

## Slide 33
Power Output, hp
stage

## Slide 34
Power Output of the blade,
Diagram Efficiency or Blade efficiency:
U
Vri
Vai
Vre
Vae
i
i
e
e
Moving blade loss Factor

## Slide 35
Losses in nozzle, Nozzle blade loss factor, 

## Slide 36
For a given shape of the blade, the efficiency is a strong function of u/Vai
For maximum efficiency:

## Slide 38: Estimation of Stage Diameters, Number of Stages

## Slide 39: Determination of first Stage Nozzle Size
The turbine in which the steam is delivered to all the revolving blades at the same time, is called Full Admission Turbine.
In a partial admission turbine steam is admitted to only some fraction of the circumference.
Degree of Partial Admission, ε
d : The mean diameter of the disc carrying the blades.
t : Pitch of the blades at the mean diameter.
z : The number of blade passages.
The exit corss-section area of the nozzle perpendicular to velocity vector, Vai.

## Slide 40
Conservation of mass:
Assign small inlet absolute angles: 14 – 150.

## Slide 41
Stages with small mean diameter are preferred.
Speed is specified by generator.
An optimum value of U/Vai should be employed.
Around 18 – 22 stages can be accommodated in a single drum.
All the quantities are known in above equations, except l & ε .
Determine l, assuming ε.or
Determine ε, assuming l.
A decrease in height or decrease in degree of partial admission will
lead to increase in energy losses in nozzle.
General Design constraints.
Nozzle height > 10mm
ε > 0.2.

## Slide 42: Estimation of Last Stage Dimensions
The dimensions of first stage and last stage are initially estimated.
The exit cross sectional are of last stage:
The exit absolute angle is taken as 900.
The condenser steam flow rate and density are found from cycle calculation.
The energy loss with exit velocity behind last stage is take as 20 to 40 kJ/kg.

## Slide 43
Mean diameter of last stage:
Shape factor,  = d/l: 2.5 – 3.0 for double flow turbine.
3.5 – 7 for single flow turbine.
Number for flows : i
Height of moving blades:

## Slide 44
d
Stages
Stage 1
Stage Z
Diameter
Variation of Diameter along a stages
Construct a diagram by laying off an arbitrary section on Abscissa.
The diameter of first state and that of a last stage are laid off as Ordinates.
The upper ends of ordinates are connected by a curve
determining diameters d of all intermediate stages.
Divide the abscissa into m number of subsections.

## Slide 45
In high pressure portion, the curve is almost horizontal.
In low pressure portion, the curve rises steeply.
The curve of velocity ratios xa = U/Va1, are assigned close to optimum
The value of xa is generally in the range of 0.56 – 0.60.

## Slide 46
d
Stages
Stage 1
Stage Z
Diameter
The curve of velocity ratios, xa for all stages is also plotted in the diagram.
The ratio d/l is selected in the range 2.5 – 3.0.
In general  decreases from stage to stage.
The degree of reaction  should increase along the stage.

## Slide 47
Calculate global available enthalpy drop for a subsection:
Local Available enthalpy drop for a sub section:
Effective available total enthalpy drop:
Calculate no. of stages, z using this effective total available enthalpy drop.

## Slide 48: CALCULATION STEPS FOR A STAGE
Steam flow rate , obtained from cycle calculation of turbine plant.
Average diameter, d (m ) for a stage obtained from a special diagram
Rotational frequency, n (rps) ,given/obtained from grid frequency
Tangential velocity at average diameter U (m/s) calculated using formula u= πdn.
Local Available enthalpy drop is known from h-s diagram
Assume a degree of reaction.
Calculate absolute velocity, (m/s)
Assume appropriate Velocity ratio.
Calculate available enthalpy drop in nozzle cascade, kJ/kg
Calculate available enthalpy drop in moving blade cascade, kJ/kg

## Slide 49
Specific volume behind the nozzle cascade(theoretical), v1t (m3/kg) , obtained from h-s diagram
Specific volume behind the moving blade cascade(theoretical), v2t (m3/kg) , obtained from h-s diagram
Theoretical steam velocity at nozzle exit, Vn m/s
Angle of velocity vector Va1, α1 assumed
Exit area of nozzle cascade, m2
Height of nozzle blades, m
Velocity coefficient of nozzle cascade.
velocity of steam exit from nozzle cascade , m/s
Relative steam velocity at entry to moving blade cascade, m/s
Angle of relative velocity vector Vw1.
Theoretical steam velocity at exit from moving blade cascade,
Height of moving blades, l2.
Chord of moving blade profile , b2 assumed.
Exit area of moving blade cascade , m2
Angle of velocity vector,2.
Velocity coefficient of moving blade cascade, ψ
Relative velocity at moving blade exit, Vr2 m/s
Absolute velocity at moving blade exit, m/s
Angle of velocity vector , 